T.J. Pemberton

PID: The Logical Control Algorithm

Anton Brosas - 301041192

8/8/2011

This report is a critical evaluation of Pemberton’s “PID: The Logical Control Algorithm”. Equations are derived and results are simulated using MATLAB Simulink.

# Introduction

A proportional-integral-derivative (PID) controller is a control loop mechanism widely used in industrial systems. It calculates an error value associated with the difference between the output and the desired setpoint and then minimizes the error by adjusting the process inputs. Instead of creating more sophisticated algorithms, this paper focuses on understanding an already naturally derived PID algorithm more clearly by looking at its’ derivation and tuning parameters (proportional gain, rate and reset time). Tuning the proportional, integral and derivative constants simultaneously can be challenging as the output is dependent on the combination of the three in a non-linear way. As many effective tuning methods exist, Pemberton discusses easier tuning procedures and uses computer simulation to demonstrate the results. In particular, the rate time to reset time ratio is one-fourth and thus, a PID controller can be controlled by proportional and integral knobs only.

# Statement of Problem

In general, derivative control is often omitted (omitting ‘D’ thus resulting in a ‘PI’ controller) since it is sensitive to the measurement noise. Operators are more easily able to visualize the effects of adjusting knobs adjusting proportional and reset action than rate action. Often this results in a “good enough” controller and the control advantage given by the derivative parameter is not realized.

The results in this paper are derived using a second-order lag plus dead-time process (see equation) and an analog simulation of an ideal PID controller using MATLAB. Zeigler-Nichols Ultimate Period (Z-N) formulas are used – for its ease of use – to provide comparisons to the ideal PID algorithm with different setpoint responses. A commonly used truncated series expansion of the exponential function eθs≅1- θs is used to derive the PID algorithm which will be discussed later in this paper. The error introduced by this approximation depends on the magnitude of θs. More specifically, the error is very small when θs is less than ½.

The equations that derive the PID algorithm are followed directly from:

- process control models (first order plus time delay and second order plus time delay) that are well accepted

- a concisely stated control objective

- truncated series expansion of exponential function

# Literature Survey

PID controller algorithms have been known for several decades (Airikka). Since the 1940s, many methods have been proposed for tuning these controllers; however, every method has brought about some limitations and/or disadvantages (Hagglund, 1998). The derivative action of a PID controller can be a mixed blessing as it can reduce the likelihood of overshoot but provide derivative kick (VanDoren, 2007). Derivative kick occurs when there is an instantaneous change in error due to a sudden change in setpoint. Since a computer algorithm will take longer to calculate a derivative than an integral, rate time tends to slow down the controller’s response time (Scrcek). Thus, the results found by Pemberton can provide more control over the overshoot and improve overall system response and efficiency.

# Development of Theory

A large number of industrial plants can be approximately modelled by first order plus time delay (FOPTD) (Tavakoli) and second order plus time delay (SOPTD) transfer functions as seen in Equation (1) and (2) respectively.

|  | CsMs=Gps=Ke-θsτs+1 | (1) |
| --- | --- | --- |

|  | C(s)M(s)=Gps=Ke-θs(τ1s+1)(τ2s+1) | (2) |
| --- | --- | --- |

where

θ is the time required for the process input to affect the process output for the first time

τX represents how fast the process responses to the process input

K represents how much the process output changes for the variation of the process input

C(s) is the process output

M(s) is the controller output to the process

GP(s) is the process transfer function

Consider a simplified unity feedback closed loop system seen in Figure 1 where R(s) is the setpoint and GC(s) is the controller transfer function.

Figure 1: Unity Feedback Closed Loop System

Since C(s) responds to a change in R(s) only after a delay of θ seconds, C(s) can be expressed as:

|  | Cs=Rse-θs | (3) |
| --- | --- | --- |

The block diagram in Figure 1 also shows that C(s) can be expressed as:

|  | Cs= R(s)Gc(s)Gp(s)1+ Gc(s)Gp(s) | (4) |
| --- | --- | --- |

Equating Equation (3) and (4) yields Equation (5):

|  | e-θs= Gc(s)Gp(s)1+ Gc(s)Gp(s) | (5) |
| --- | --- | --- |

Substituting the general SOPTD model as our process transfer function, (5) becomes:

|  | e-θs= Gc(s)Ke-θs(τ1s+1)τ2s+11+ Gc(s)Ke-θs(τ1s+1)τ2s+1 | (6) |
| --- | --- | --- |

This can be further simplified:

|  | e-θs= Gc(s)Ke-θs(τ1s+1)τ2s+1+ Gc(s)Ke-θs | (7) |
| --- | --- | --- |

Dividing by e-θs:

|  | (τ1s+1)τ2s+1+ Gc(s)Ke-θs= Gc(s)K | (8) |
| --- | --- | --- |

Dividing by K:

|  | Gcs= (τ1s+1)τ2s+1K+ Gc(s)e-θs | (9) |
| --- | --- | --- |

Given Equation (9), the unity feedback closed loop system can be represented as seen in Figure 2.

Figure 2: Expanded Unity Feedback Closed Loop System

GC(s) can also be expressed as:

|  | Gcs= M(s)E(s)=(τ1s+1)τ2s+1K[1- e-θs] | (10) |
| --- | --- | --- |

Noting that M(s) = GC(s) (relating Figure (1) and Figure (2)):

|  | Ms= (τ1s+1)τ2s+1K+ M(s)e-θs | (11) |
| --- | --- | --- |

A commonly used truncated series expansion of the exponential function eθs≅1- θs is used to derive the PID algorithm. Substituting this into Equation (10) yields:

|  | Gcs=(τ1s+1)τ2s+1K[1-(1- θs)]=1Kθs[τ1τ2s2+τ1+τ2s+1] | (12) |
| --- | --- | --- |

Multiplying the numerator and denominator by τ1+τ2s:

|  | Gcs=τ1+τ2Kθ1+1(τ1+τ2)s+τ1τ2sτ1+τ2 | (13) |
| --- | --- | --- |

where

| Kc | τi | τr |
| --- | --- | --- |
| τ1+τ2/ Kθ | τ1+τ2 | τ1τ2/(τ1+τ2) |

Table 1: Natural PID Parameters

The generalized form of controller is seen in (14).

|  | Gcs=Kc1+1τis+τrs | (14) |
| --- | --- | --- |

Pemberton states the relationship between reset time and rate time has a reoccurrence of the value 0.25, suggesting the possibility that for many applications the rate time might be arbitrarily set at one-fourth the reset time. The Zeigler-Nichols Ultimate Period (closed loop) formulae for PID, PI and modified PID are outlined in Table 2.

|  | Kc | τi | τr |
| --- | --- | --- | --- |
| Z-N PID | Ku/1.7 | Tu/2 | Tu/8 |
| Z-N PI | Ku/2.2 | Tu/1.2 |  |
| Modified Z-N PID | Ku/2.2 | Tu/1.2 | τi/4 |

Table 2: Z-N Ultimate Period Tuning Parameters

The Modified Z-N PID is derived from the basic Z-N PI controller and then adding a derivate term by setting τr= τi/4.

Although it is not mentioned, Ku is obtained by setting τi and τr = 0. Then, Kc is increased until the process output C(s) is a sustained periodic oscillation. When sustained oscillation is obtained, this critical Kc  value is Ku – ultimate gain. Tu is the measured period of oscillation – ultimate period.

The ideal PID algorithm found in Equation (14) and the parameters found in Table 1 are compared to ZN parameters in the Simulation Studies section.

# Simulation Studies

## Z-N Ultimate Period Closed Loop Tuning

Using Z-N PID, PI and Modified PID closed loop tuning formulae, the following results were found for a SOPTD process transfer function with τ1/τ2 varying from 0.1 to 1.0 and θ/τ2 varying from 0.2 to 1.0 and θ=0.25 seconds and K = 1 in Equation (2).

| Figure 3: τ1τ2=0.1 θτ2=0.2 | Figure 4: τ1τ2=0.5 θτ2=0.2 |
| --- | --- |
| Figure 5: τ1τ2=1.0 θτ2=0.2 | Figure 6: τ1τ2=0.1 θτ2=0.4 |

| Figure 7: τ1τ2=0.5 θτ2=0.4 | Figure 8: τ1τ2=1.0 θτ2=0.4 |
| --- | --- |
| Figure 9: τ1τ2=0.2 θτ2=1.0 | Figure 10: τ1τ2=1.0 θτ2=1.0 |

## Ideal PID Algorithm

Recall the parameters for the naturally derived PID algorithm:

| Kc | τi | τr |
| --- | --- | --- |
| τ1+τ2/ Kθ | τ1+τ2 | τ1τ2/(τ1+τ2) |

Figure 11: Constants in front of KC

Multiplying factors of 1/2 and 2/3 for Kc are tested as seen in Figure 11. A factor of 2/3 proves to have an appropriate percent overshoot and rise time.

|  | Kc | τi | τr |
| --- | --- | --- | --- |
| Ideal PID | 2τ1+τ2/3Kθ | τ1+τ2 | τ1τ2/(τ1+τ2) |
| Modified Ideal PID | 2τ1+τ2/3Kθ | τ1+τ2 | τi/4 |

Table 3: Ideal PID Algorithm Tuning Parameters

Using the parameters in Table 3 above, comparisons were made for Z-N PI, Ideal PID and Modified Ideal PID tuning parameters for a SOPTD process transfer function with τ1/τ2 varying from 0.1 to 1.0 and θ/τ2 varying from 0.2 to 1.0 and θ=0.25 seconds and K = 1 in Equation (2).

| Figure 12: τ1τ2=0.1 θτ2=0.2 | Figure 13: τ1τ2=0.5 θτ2=0.2 |
| --- | --- |
| Figure 14: τ1τ2=1.0 θτ2=0.2 | Figure 15: τ1τ2=0.1 θτ2=0.4 |

| Figure 16: τ1τ2=0.5 θτ2=0.4 | Figure 17: τ1τ2=1.0 θτ2=0.4 |
| --- | --- |
| Figure18: τ1τ2=0.2 θτ2=1.0 | Figure19: τ1τ2=1.0 θτ2=1.0 |

# Discussion

## Z-N Ultimate Period Closed Loop Tuning

Figures 3, 4, 5, 7 and 8 best represents proper tuning parameters using the Z-N Ultimate Period formulae. Looking closely, it can be see that the Modified Z-N PID has the fastest rise time, smallest percent overshoot and shortest settling time, followed by the Z-N PID and the Z-N PI curves respectively.  Thus, the rate time to reset time ratio of 0.25 added to a Z-N PI controller proved to give better results than the conventional Z-N PID parameters.

Figures 6, 9, and 10 show signs of deviation from the trends seen in Figure 4, 5, 7 and 8. The reasons for this may be

- incorrect ultimate gain

- incorrect ultimate period

- plant characteristics, GP(s), that cause some instability

## Ideal PID Algorithm

Figure 12, 13, 14, 16 and 17 best represent the capability of using the derived tuning parameters as outlined in Table 3. The Modified Ideal PID curve has the shortest rise time, smallest percent overshoot and shortest settling time, followed by the Ideal PID and the Z-N PI curves respectively. Thus, the rate time to reset time ratio of 0.25 proved to give better results than the conventional naturally derived PID parameters.

Figures 15, 18 and 19 show signs of deviation from the trends seen in Figure 12, 13, 14, 16 and 17. It is noted that Figures 6 and 15, 9 and 18, and 10 and 19 use the same values of τ1 and τ2. It can be concluded that it is the plant (GP(s)) that is the cause for an inefficient controller.

At this time, it is unsure why these trends exist for those specific plant transfer function characteristics. Pemberton does not mention or make visible this nonconformity.

## Commercial Controllers

Pemberton mentions the feasibility of integrating the rate time to reset ratio in electronic, pneumatic and digital controllers. Although the implementation and actual ratio value will vary from one type to the other, it is mentioned that is has been successfully implemented into electronic control and digital control, noting that only proportional and reset time controlling parameters are needed. The relation between the reset and rate time has not been attempted in pneumatic controllers as it appears that mechanical linkages would be required.

# Conclusion

This paper focused on understanding an already natural PID algorithm more clearly by looking at its’ derivation and tuning parameters (proportional gain, rate and reset time). Tuning the proportional, integral and derivative constants simultaneously can be challenging as the output is dependent on the combination of the three in a non-linear way. As many effective tuning methods exist, Pemberton discusses easier tuning procedures and uses computer simulation to demonstrate the results. In particular, the rate time to reset time ratio is one-fourth and thus, a PID controller can be controlled by proportional and integral knobs only. This was proven through simulations using Z-N Ultimate Period closed loop tuning parameters and naturally derived PID tuning parameters. In both cases, the rate time to reset time of 0.25 provided a shorter rise time, smaller percent overshoot and shorter settling time than the conventional PID tuning parameters.

# List of References

Airikka, P. (n.d.). The PID Controller: Algorithm and Implementation.

Hagglund, K. A. (1998). Automatic Tuning of PID Controllers.

Pemberton, T. (1972). PID: The Logical Control Algorithm.

Scrcek, W. Y. (n.d.). "A Real Time Approach to Process Control".

Tavakoli, S. T. (n.d.). Optimal Tuning of PID Controllers for First Order Plus Time Delay Models Using Dimensional Analysis.

VanDoren. (2007). The Three Faces of PID.

# Appendices

See attached .m .bmp and .xlsx files